Function

Measuring-sensor Z50

for flow-meter M23

# Functional parts:

A)	flow-meter M23 with monostable magnetic float

B)	measuring-Sensor Z50

C)	connection

D)	dovetail to mount Z50

E)	clamping screw to hold the measuring sensor in position

# Advantages:

	simple assembling

	analoge outgoing signal 4 – 20 mA

	24 V DC power supply

	protected by IP 65

	body of PVC-U

	connection through DIN plug

The measuring-sensor Z50, which is mounted on the flow-meter M23, supplies in proportional to the position of the magnetic float an analog outgoing signal of 4-20mA. This signal can be used directly without any additional plotting station. This means a really competitive possibility for the remotely -indication or -regulation of the flow rates. Of course Z50 can be assembled later into the application. Required is just a monostable magnetic float in the flow-meter. For the best possible reproducibility we offer two different measuring sensors Z50, which are optimal adapted for the different measuring ranges.

## Assembling-guide

- put the measuring-sensor on the dovetail of the flow-meter

- adjust the marking on the measuring-sensor with the 50% marking of the scale on the flow-meter

- tight the clamping screw

- put off and wire the plug acc. to default

## Technical datas

| measuring-sensor type measuring range l/h line-voltage | 24 V ± 10 % |
| --- | --- |
| current consumption | ca. 6 mA 4 mA at the power interface |
| apparent power resistor | min. 0 Ohm, max. 250 Ohm |
| current-exit | 4-20 mA max. voltage increase + 5 V |
| electr. tolerance | max. + 1-3% from measuring value |
| protection | IP 65 acc. DIN 40050 |
| allowed ambient temperature | 0 °C – + 50°C |
| connection | DIN plug DIN 43650 |
| protection device | reverse battery protection / intigrated noisefilter for the operating voltage |

15 -150

Z50/1                          100-1000

Part-no: ON REQUEST            1200-12000

2000-20000

3000-30000

Z50/2                      50-500

Part-no: ON REQUEST            200-2000

300-3000

## Electrical connection:

Pin 1 :  operating voltage 24 V                       1 Ø                                             + 24 V

Pin 2 :  outgoing signal 4-20 mA                    2 Ø                                              4 – 20 mA-------R

Pin 3 :  0 V                                                      3 Ø